## Example 1
Pipe Network Analysis
| CheGuide.com | [7 empty] | Date | 17-Dec-15
| Chemical Engineer's Guide | [7 empty] | By | CheGuide
A water supply distribution system is shown in the figure below. All pipes are cast iron with lengths
and diameters as provided in table below. Perform pipe network analysis and calculate water flow in all
branches.
[8 empty] | Pipe | Length | Diameter | e/D
[9 empty] | m | m
[8 empty] | 1 | 300 | 0.3 | 0.00087
[8 empty] | 2 | 250 | 0.25 | 0.00104
[8 empty] | 5 | 350 | 0.2 | 0.0013
[8 empty] | 3 | 125 | 0.2 | 0.0013
[8 empty] | 6 | 350 | 0.2 | 0.0013
[8 empty] | 7 | 125 | 0.2 | 0.0013
[8 empty] | 4 | 300 | 0.2 | 0.0013
[8 empty] | 8 | 125 | 0.15 | 0.00173
[8 empty] | 9 | 350 | 0.2 | 0.0013
[8 empty] | 10 | 125 | 0.15 | 0.00173
Iteration
1 | Pipe | Flow | Length | Diameter | e/D | Velocity | Reynold's | Friction |  | Head Loss
|  | m3/s | m | m |  | m/s | Number | Factor, f | K | hL | nHL/Q
| 1 | 0.2 | 300 | 0.3 | 0.00087 | 2.8294 | 848826.3632 | 0.019481 | 198.7214 | 7.9489 | 79.4886
| 2 | 0.1 | 250 | 0.25 | 0.00104 | 2.0372 | 509295.8179 | 0.020516 | 433.9696 | 4.3397 | 86.7939
| 5 | 0.08 | 350 | 0.2 | 0.0013 | 2.5465 | 509295.8179 | 0.021559 | 1948.3748 | 12.4696 | 311.74
| 3 | 0.12 | 125 | 0.2 | 0.0013 | 3.8197 | 763943.7268 | 0.021378 | 690.0017 | 9.936 | 165.6004
| 6 | 0.07 | 350 | 0.2 | 0.0013 | 2.2282 | 445633.8407 | 0.021634 | 1955.1143 | 9.5801 | 273.716
| 7 | 0.03 | 125 | 0.2 | 0.0013 | 0.95493 | 190985.9317 | 0.022355 | 721.5239 | 0.64937 | 43.2914
| 4 | 0.1 | 300 | 0.2 | 0.0013 | 3.1831 | 636619.7724 | 0.021452 | 1661.7202 | 16.6172 | 332.344
| 8 | 0.05 | 125 | 0.15 | 0.00173 | 2.8294 | 424413.1816 | 0.023146 | 3148.0557 | 7.8701 | 314.8056
| 9 | 0.05 | 350 | 0.2 | 0.0013 | 1.5915 | 318309.8862 | 0.021863 | 1975.8113 | 4.9395 | 197.5811
| 10 | 0.1 | 125 | 0.15 | 0.00173 | 5.6588 | 848826.3632 | 0.02287 | 3110.6369 | 31.1064 | 622.1274
| Coefficient Matrix |  |  |  |  | Inverse |  |  |  | F | DQ
|  | 979.0325 | -165.6004 | -314.8056 |  | 0.0011915 | 0.0003646 | 0.00033723 |  | 10.9422 | 0.00066131
|  | -165.6004 | 794.3478 | -273.716 |  | 0.0003646 | 0.0014608 | 0.00036545 |  | 6.3971 | -0.002605
|  | -314.8056 | -273.716 | 1408.2301 |  | 0.00033723 | 0.00036545 | 0.00085653 |  | -43.617 | -0.031331
Iteration
2 | Pipe | Flow | Length | Diameter | e/D | Velocity | Reynold's | Friction
|  | m3/s | m | m |  | m/s | Number | Factor, f | K | hL | nHL/Q
| 1 | 0.20066 | 300 | 0.3 | 0.00087 | 2.8388 | 851633.0692 | 0.019479 | 198.707 | 8.0009 | 79.7456
| 2 | 0.099339 | 250 | 0.25 | 0.00104 | 2.0237 | 505927.7706 | 0.02052 | 434.0535 | 4.2833 | 86.2366
| 5 | 0.077395 | 350 | 0.2 | 0.0013 | 2.4636 | 492711.754 | 0.021577 | 1949.976 | 11.6803 | 301.8367
| 3 | 0.12327 | 125 | 0.2 | 0.0013 | 3.9237 | 784737.8498 | 0.021368 | 689.6812 | 10.4794 | 170.029
| 6 | 0.041274 | 350 | 0.2 | 0.0013 | 1.3138 | 262755.7011 | 0.022024 | 1990.4207 | 3.3907 | 164.3035
| 7 | 0.027395 | 125 | 0.2 | 0.0013 | 0.87201 | 174401.8679 | 0.022465 | 725.0787 | 0.54416 | 39.727
| 4 | 0.099339 | 300 | 0.2 | 0.0013 | 3.162 | 632409.7133 | 0.021455 | 1661.9455 | 16.4004 | 330.191
| 8 | 0.018007 | 125 | 0.15 | 0.00173 | 1.019 | 152850.1649 | 0.023991 | 3263.0926 | 1.0581 | 117.5186
| 9 | 0.081331 | 350 | 0.2 | 0.0013 | 2.5889 | 517772.0896 | 0.021551 | 1947.5929 | 12.8829 | 316.8011
| 10 | 0.068669 | 125 | 0.15 | 0.00173 | 3.8858 | 582876.7587 | 0.022999 | 3128.157 | 14.7504 | 429.612
| Coefficient Matrix |  |  |  |  | Inverse |  |  |  | F | DQ
|  | 783.7207 | -170.029 | -117.5186 |  | 0.0013978 | 0.00040624 | 0.00022467 |  | 3.2614 | 0.0038082
|  | -170.029 | 675.8962 | -164.3035 |  | 0.00040624 | 0.0016574 | 0.00031127 |  | 1.6456 | 0.0020863
|  | -117.5186 | -164.3035 | 1028.2352 |  | 0.00022467 | 0.00031127 | 0.001048 |  | -6.3163 | -0.0053742
Iteration
3 | Pipe | Flow | Length | Diameter | e/D | Velocity | Reynold's | Friction
|  | m3/s | m | m |  | m/s | Number | Factor, f | K | hL | nHL/Q
| 1 | 0.20447 | 300 | 0.3 | 0.00087 | 2.8927 | 867795.7408 | 0.019471 | 198.6253 | 8.3041 | 81.2257
| 2 | 0.09553 | 250 | 0.25 | 0.00104 | 1.9461 | 486532.5647 | 0.020544 | 434.5576 | 3.9658 | 83.027
| 5 | 0.079481 | 350 | 0.2 | 0.0013 | 2.53 | 505993.7993 | 0.021563 | 1948.6859 | 12.3104 | 309.7683
| 3 | 0.12499 | 125 | 0.2 | 0.0013 | 3.9785 | 795699.8118 | 0.021363 | 689.5186 | 10.7717 | 172.3634
| 6 | 0.033813 | 350 | 0.2 | 0.0013 | 1.0763 | 215260.5255 | 0.022221 | 2008.1851 | 2.296 | 135.8057
| 7 | 0.029481 | 125 | 0.2 | 0.0013 | 0.93842 | 187683.9131 | 0.022375 | 722.1872 | 0.62769 | 42.5821
| 4 | 0.09553 | 300 | 0.2 | 0.0013 | 3.0408 | 608165.7059 | 0.021472 | 1663.2986 | 15.1794 | 317.7913
| 8 | 0.0088248 | 125 | 0.15 | 0.00173 | 0.49938 | 74907.3147 | 0.025146 | 3420.2062 | 0.26636 | 60.3653
| 9 | 0.086706 | 350 | 0.2 | 0.0013 | 2.7599 | 551985.2199 | 0.021518 | 1944.6627 | 14.6197 | 337.2264
| 10 | 0.063294 | 125 | 0.15 | 0.00173 | 3.5817 | 537259.2515 | 0.023033 | 3132.7649 | 12.5504 | 396.5727
| Coefficient Matrix |  |  |  |  | Inverse |  |  |  | F | DQ
|  | 714.7727 | -172.3634 | -60.3653 |  | 0.001516 | 0.00042871 | 0.00016101 |  | 0.33574 | 0.00048518
|  | -172.3634 | 660.5194 | -135.8057 |  | 0.00042871 | 0.0016821 | 0.00027346 |  | 0.12962 | 0.00022713
|  | -60.3653 | -135.8057 | 929.9702 |  | 0.00016101 | 0.00027346 | 0.0011257 |  | -0.49305 | -0.00046552
Iteration
4 | Pipe | Flow | Length | Diameter | e/D | Velocity | Reynold's | Friction
|  | m3/s | m | m |  | m/s | Number | Factor, f | K | hL | nHL/Q
| 1 | 0.20495 | 300 | 0.3 | 0.00087 | 2.8995 | 869854.9042 | 0.01947 | 198.6151 | 8.3431 | 81.4142
| 2 | 0.095045 | 250 | 0.25 | 0.00104 | 1.9362 | 484061.5687 | 0.020547 | 434.6244 | 3.9262 | 82.618
| 5 | 0.079708 | 350 | 0.2 | 0.0013 | 2.5372 | 507439.7728 | 0.021561 | 1948.5492 | 12.38 | 310.6317
| 3 | 0.12525 | 125 | 0.2 | 0.0013 | 3.9867 | 797342.5835 | 0.021362 | 689.4945 | 10.8158 | 172.7133
| 6 | 0.03312 | 350 | 0.2 | 0.0013 | 1.0543 | 210850.9731 | 0.022243 | 2010.1949 | 2.2051 | 133.1569
| 7 | 0.029708 | 125 | 0.2 | 0.0013 | 0.94565 | 189129.8866 | 0.022366 | 721.8942 | 0.63714 | 42.8927
| 4 | 0.095045 | 300 | 0.2 | 0.0013 | 3.0254 | 605076.9609 | 0.021475 | 1663.4782 | 15.0272 | 316.2115
| 8 | 0.0078741 | 125 | 0.15 | 0.00173 | 0.44558 | 66837.5493 | 0.025395 | 3453.9388 | 0.21415 | 54.3934
| 9 | 0.087171 | 350 | 0.2 | 0.0013 | 2.7747 | 554948.7989 | 0.021516 | 1944.4246 | 14.7753 | 338.9955
| 10 | 0.062829 | 125 | 0.15 | 0.00173 | 3.5554 | 533307.8128 | 0.023036 | 3133.1984 | 12.3682 | 393.7105
| Coefficient Matrix |  |  |  |  | Inverse |  |  |  | F | DQ
|  | 707.3503 | -172.7133 | -54.3934 |  | 0.0015309 | 0.00043189 | 0.00015298 |  | 0.0086155 | 1.2987e-05
|  | -172.7133 | 659.3946 | -133.1569 |  | 0.00043189 | 0.001684 | 0.0002692 |  | 0.0038266 | 6.8998e-06
|  | -54.3934 | -133.1569 | 920.2563 |  | 0.00015298 | 0.0002692 | 0.0011346 |  | -0.012129 | -1.1414e-05
Iteration
5 | Pipe | Flow | Length | Diameter | e/D | Velocity | Reynold's | Friction
|  | m3/s | m | m |  | m/s | Number | Factor, f | K | hL | nHL/Q
| 1 | 0.20497 | 300 | 0.3 | 0.00087 | 2.8997 | 869910.0227 | 0.01947 | 198.6148 | 8.3442 | 81.4193
| 2 | 0.095032 | 250 | 0.25 | 0.00104 | 1.936 | 483995.4264 | 0.020547 | 434.6262 | 3.9252 | 82.607
| 5 | 0.079715 | 350 | 0.2 | 0.0013 | 2.5374 | 507483.6985 | 0.021561 | 1948.5451 | 12.3821 | 310.6579
| 3 | 0.12525 | 125 | 0.2 | 0.0013 | 3.9869 | 797381.3356 | 0.021362 | 689.494 | 10.8169 | 172.7215
| 6 | 0.033102 | 350 | 0.2 | 0.0013 | 1.0537 | 210734.3826 | 0.022244 | 2010.2491 | 2.2027 | 133.0869
| 7 | 0.029715 | 125 | 0.2 | 0.0013 | 0.94587 | 189173.8123 | 0.022366 | 721.8854 | 0.63743 | 42.9022
| 4 | 0.095032 | 300 | 0.2 | 0.0013 | 3.025 | 604994.283 | 0.021475 | 1663.483 | 15.0231 | 316.1692
| 8 | 0.0078497 | 125 | 0.15 | 0.00173 | 0.4442 | 66630.4258 | 0.025402 | 3454.8963 | 0.21288 | 54.2399
| 9 | 0.087183 | 350 | 0.2 | 0.0013 | 2.7751 | 555021.4637 | 0.021515 | 1944.4188 | 14.7791 | 339.0388
| 10 | 0.062817 | 125 | 0.15 | 0.00173 | 3.5547 | 533210.9265 | 0.023036 | 3133.2091 | 12.3637 | 393.6403
| Coefficient Matrix |  |  |  |  | Inverse |  |  |  | F | DQ
|  | 707.1569 | -172.7215 | -54.2399 |  | 0.0015313 | 0.00043197 | 0.00015277 |  | 0.00014153 | 2.2181e-07
|  | -172.7215 | 659.3684 | -133.0869 |  | 0.00043197 | 0.0016841 | 0.00026908 |  | 8.5165e-05 | 1.4869e-07
|  | -54.2399 | -133.0869 | 920.0059 |  | 0.00015277 | 0.00026908 | 0.0011349 |  | -0.00020762 | -1.9109e-07
50 lps
150 lps
100 lps
300 lps
1
3
6
2
5
9
4
8
7
10
I
II
III

## Example 2
Pipe Network Analysis
| CheGuide.com | [7 empty] | Date | 17-Dec-15
| Chemical Engineer's Guide | [7 empty] | By | CheGuide
A water supply distribution system is shown in the figure below. All pipes are cast iron with lengths
and diameters as provided in table below. Perform pipe network analysis and calculate water flow in all
branches.
[8 empty] | Pipe | Length | Diameter | e/D
[9 empty] | m | m
[8 empty] | 1 | 1000 | 0.4 | 0.00087
[8 empty] | 2 | 2000 | 0.45 | 0.00104
[8 empty] | 3 | 1000 | 0.3 | 0.0013
[8 empty] | 4 | 2000 | 0.3 | 0.0013
[8 empty] | 5 | 1000 | 0.4 | 0.0013
[8 empty] | 6 | 750 | 0.3 | 0.0013
[8 empty] | 7 | 2200 | 0.3 | 0.0013
[8 empty] | 8 | 2000 | 0.3 | 0.00173
[8 empty] | 9 | 500 | 0.25 | 0.0013
[8 empty] | 10 | 2200 | 0.25 | 0.00173
Iteration
1 | Pipe | Flow | Length | Diameter | e/D | Velocity | Reynold's | Friction |  | Head Loss
|  | m3/s | m | m |  | m/s | Number | Factor, f | K | hL | nHL/Q
| 1 | 0.1 | 1000 | 0.4 | 0.00087 | 0.79577 | 318309.8862 | 0.02013 | 162.4298 | 1.6243 | 32.486
| 2 | 0.2 | 2000 | 0.45 | 0.00104 | 1.2575 | 565884.2421 | 0.020456 | 183.1938 | 7.3278 | 73.2775
| 3 | 0.03 | 1000 | 0.3 | 0.0013 | 0.42441 | 127323.9545 | 0.022911 | 779.0406 | 0.70114 | 46.7424
| 4 | 0.03 | 2000 | 0.3 | 0.0013 | 0.42441 | 127323.9545 | 0.022911 | 1558.0812 | 1.4023 | 93.4849
| 5 | 0.07 | 1000 | 0.4 | 0.0013 | 0.55704 | 222816.9203 | 0.022185 | 179.0095 | 0.87715 | 25.0613
| 6 | 0.08 | 750 | 0.3 | 0.0013 | 1.1318 | 339530.5453 | 0.021814 | 556.2992 | 3.5603 | 89.0079
| 7 | 0.02 | 2200 | 0.3 | 0.0013 | 0.28294 | 84882.6363 | 0.023662 | 1770.0356 | 0.70801 | 70.8014
| 8 | 0.17 | 2000 | 0.3 | 0.00173 | 2.405 | 721502.4087 | 0.022921 | 1558.7595 | 45.0481 | 529.9782
| 9 | 0.02 | 500 | 0.25 | 0.0013 | 0.40744 | 101859.1636 | 0.023297 | 985.5776 | 0.39423 | 39.4231
| 10 | 0.02 | 2200 | 0.25 | 0.00173 | 0.40744 | 101859.1636 | 0.024572 | 4573.8691 | 1.8295 | 182.9548
| Coefficient Matrix |  |  |  |  | Inverse |  |  |  | F | DQ
|  | 245.9908 | -46.7424 | -93.4849 |  | 0.0047201 | 0.0002761 | 0.0015852 |  | -5.0023 | -0.041824
|  | -46.7424 | 799.0985 | 0 |  | 0.0002761 | 0.0012676 | 9.2726e-05 |  | -46.5708 | -0.060726
|  | -93.4849 | 0 | 278.3555 |  | 0.0015852 | 9.2726e-05 | 0.0041249 |  | -3.3774 | -0.02618
Iteration
2 | Pipe | Flow | Length | Diameter | e/D | Velocity | Reynold's | Friction |  | Head Loss
|  | m3/s | m | m |  | m/s | Number | Factor, f | K | hL | nHL/Q
| 1 | 0.14182 | 1000 | 0.4 | 0.00087 | 1.1286 | 451438.2215 | 0.019838 | 160.0744 | 3.2197 | 45.4046
| 2 | 0.15818 | 2000 | 0.45 | 0.00104 | 0.99455 | 447547.9441 | 0.020598 | 184.4614 | 4.6152 | 58.3549
| 3 | 0.048902 | 1000 | 0.3 | 0.0013 | 0.69182 | 207546.8833 | 0.02226 | 756.9198 | 1.8101 | 74.0299
| 4 | 0.045644 | 2000 | 0.3 | 0.0013 | 0.64573 | 193717.8793 | 0.022338 | 1519.1237 | 3.1649 | 138.6769
| 5 | 0.09618 | 1000 | 0.4 | 0.0013 | 0.76537 | 306149.812 | 0.021894 | 176.6605 | 1.6342 | 33.9823
| 6 | 0.05382 | 750 | 0.3 | 0.0013 | 0.7614 | 228420.0231 | 0.022159 | 565.108 | 1.6369 | 60.8285
| 7 | 0.04618 | 2200 | 0.3 | 0.0013 | 0.65331 | 195993.1585 | 0.022325 | 1670.0297 | 3.5615 | 154.2433
| 8 | 0.10927 | 2000 | 0.3 | 0.00173 | 1.5459 | 463775.0328 | 0.023101 | 1570.9702 | 18.7588 | 343.3337
| 9 | -0.040726 | 500 | 0.25 | 0.0013 | 0.82965 | 207413.6874 | 0.022261 | 941.7591 | -1.562 | 76.7074
| 10 | -0.040726 | 2200 | 0.25 | 0.00173 | 0.82965 | 207413.6874 | 0.023661 | 4404.388 | -7.305 | 358.7425
| Coefficient Matrix |  |  |  |  | Inverse |  |  |  | F | DQ
|  | 316.4663 | -74.0299 | -138.6769 |  | 0.0038396 | 0.00033331 | 0.0013733 |  | -0.040713 | -0.0023091
|  | -74.0299 | 852.8135 | 0 |  | 0.00033331 | 0.0012015 | 0.00011921 |  | -8.0817 | -0.009677
|  | -138.6769 | 0 | 387.7309 |  | 0.0013733 | 0.00011921 | 0.0030703 |  | 0.39391 | 0.00019006
Iteration
3 | Pipe | Flow | Length | Diameter | e/D | Velocity | Reynold's | Friction |  | Head Loss
|  | m3/s | m | m |  | m/s | Number | Factor, f | K | hL | nHL/Q
| 1 | 0.14413 | 1000 | 0.4 | 0.00087 | 1.147 | 458788.1994 | 0.019827 | 159.9806 | 3.3235 | 46.1168
| 2 | 0.15587 | 2000 | 0.45 | 0.00104 | 0.98003 | 441014.6303 | 0.020607 | 184.5493 | 4.4836 | 57.5305
| 3 | 0.05627 | 1000 | 0.3 | 0.0013 | 0.79606 | 238817.253 | 0.022115 | 751.9648 | 2.381 | 84.6261
| 4 | 0.048143 | 2000 | 0.3 | 0.0013 | 0.68108 | 204324.502 | 0.022278 | 1515.0138 | 3.5114 | 145.8741
| 5 | 0.09599 | 1000 | 0.4 | 0.0013 | 0.76386 | 305544.8229 | 0.021895 | 176.6733 | 1.6279 | 33.9177
| 6 | 0.05401 | 750 | 0.3 | 0.0013 | 0.76409 | 229226.6751 | 0.022156 | 565.0167 | 1.6482 | 61.0334
| 7 | 0.04599 | 2200 | 0.3 | 0.0013 | 0.65062 | 195186.5065 | 0.022329 | 1670.3841 | 3.533 | 153.641
| 8 | 0.099597 | 2000 | 0.3 | 0.00173 | 1.409 | 422704.6925 | 0.023148 | 1574.1725 | 15.6152 | 313.5671
| 9 | -0.050403 | 500 | 0.25 | 0.0013 | 1.0268 | 256698.0959 | 0.022046 | 932.6504 | -2.3693 | 94.0159
| 10 | -0.050403 | 2200 | 0.25 | 0.00173 | 1.0268 | 256698.0959 | 0.023475 | 4369.6458 | -11.1007 | 440.4826
| Coefficient Matrix |  |  |  |  | Inverse |  |  |  | F | DQ
|  | 334.1475 | -84.6261 | -145.8741 |  | 0.0036694 | 0.00033294 | 0.0013569 |  | -0.029654 | -2.8665e-05
|  | -84.6261 | 932.6918 | 0 |  | 0.00033294 | 0.0011024 | 0.00012312 |  | 0.23576 | 0.00025017
|  | -145.8741 | 0 | 394.4662 |  | 0.0013569 | 0.00012312 | 0.0030369 |  | 0.0012184 | -7.5114e-06
Iteration
4 | Pipe | Flow | Length | Diameter | e/D | Velocity | Reynold's | Friction |  | Head Loss
|  | m3/s | m | m |  | m/s | Number | Factor, f | K | hL | nHL/Q
| 1 | 0.14416 | 1000 | 0.4 | 0.00087 | 1.1472 | 458879.4423 | 0.019826 | 159.9795 | 3.3248 | 46.1257
| 2 | 0.15584 | 2000 | 0.45 | 0.00104 | 0.97985 | 440933.5256 | 0.020608 | 184.5504 | 4.4819 | 57.5202
| 3 | 0.055991 | 1000 | 0.3 | 0.0013 | 0.79211 | 237633.8364 | 0.02212 | 752.131 | 2.3579 | 84.2254
| 4 | 0.048164 | 2000 | 0.3 | 0.0013 | 0.68138 | 204414.2797 | 0.022277 | 1514.9806 | 3.5144 | 145.935
| 5 | 0.095997 | 1000 | 0.4 | 0.0013 | 0.76392 | 305568.7325 | 0.021895 | 176.6728 | 1.6281 | 33.9202
| 6 | 0.054003 | 750 | 0.3 | 0.0013 | 0.76398 | 229194.7957 | 0.022156 | 565.0203 | 1.6478 | 61.0253
| 7 | 0.045997 | 2200 | 0.3 | 0.0013 | 0.65073 | 195218.3859 | 0.022329 | 1670.37 | 3.5341 | 153.6649
| 8 | 0.099848 | 2000 | 0.3 | 0.00173 | 1.4126 | 423766.452 | 0.023146 | 1574.0825 | 15.6929 | 314.3368
| 9 | -0.050152 | 500 | 0.25 | 0.0013 | 1.0217 | 255423.9845 | 0.022051 | 932.8459 | -2.3464 | 93.5689
| 10 | -0.050152 | 2200 | 0.25 | 0.00173 | 1.0217 | 255423.9845 | 0.023479 | 4370.3895 | -10.9927 | 438.3709
| Coefficient Matrix |  |  |  |  | Inverse |  |  |  | F | DQ
|  | 333.8063 | -84.2254 | -145.935 |  | 0.0036737 | 0.00033253 | 0.0013588 |  | -0.00070636 | -1.1981e-06
|  | -84.2254 | 930.5019 | 0 |  | 0.00033253 | 0.0011048 | 0.000123 |  | 0.0040723 | 4.268e-06
|  | -145.935 | 0 | 394.5454 |  | 0.0013588 | 0.000123 | 0.0030372 |  | 3.1408e-05 | -3.6356e-07
150 lps
100 lps
300 lps
1
3
6
2
5
9
4
7
8
10
I
50 lps
III
II

## Example 3
Pipe Network Analysis
| CheGuide.com | [12 empty] | Date | 17-Dec-15
| Chemical Engineer's Guide | [12 empty] | By | CheGuide
Solve for water piping network as shown in diagram. Hazen-Williams coefficient, C for each pipe is provided in table below.
[10 empty] | Pipe | Diameter | Length | C
[11 empty] | mm | m
[10 empty] | 1 | 1000 | 1000 | 100
[10 empty] | 2 | 750 | 925 | 100
[10 empty] | 3 | 750 | 1000 | 100
[10 empty] | 4 | 750 | 925 | 100
[10 empty] | 5 | 500 | 350 | 100
[10 empty] | 6 | 500 | 671 | 100
[10 empty] | 7 | 500 | 400 | 100
[10 empty] | 8 | 500 | 650 | 100
[10 empty] | 9 | 750 | 1000 | 120
[10 empty] | 10 | 1000 | 1000 | 120
[10 empty] | 11 | 1000 | 925 | 120
[10 empty] | 12 | 1000 | 800 | 120
[10 empty] | 13 | 750 | 763 | 120
[10 empty] | 14 | 1000 | 650 | 120
[10 empty] | 15 | 750 | 400 | 120
[10 empty] | 16 | 750 | 125 | 120
[10 empty] | 17 | 750 | 400 | 120
[10 empty] | 18 | 500 | 125 | 120
[10 empty] | 19 | 500 | 800 | 120
[10 empty] | 20 | 500 | 125 | 120
[10 empty] | 21 | 500 | 800 | 120
[10 empty] | 22 | 500 | 1000 | 120
Iteration
1 | Pipe | Flow | Diameter | Length | C | Head Loss
|  | m3/s | mm | m |  | HL, m | nHL/Q | Coefficient Matrix | [7 empty] | F
| 1 | 1 | 1000 | 1000 | 100 | 2.1289 | 3.9385 | 127.2235 | -67.82 | -40.6762 | 0 | 0 | 0 | 0 |  | -280.0535
| 2 | 6 | 750 | 925 | 100 | 219.9569 | 67.82 | -67.82 | 104.0453 | 0 | -11.4104 | 0 | 0 | 0 |  | 229.2603
| 3 | 3 | 750 | 1000 | 100 | 65.9615 | 40.6762 | -40.6762 | 0 | 403.4669 | -74.8627 | 0 | 0 | 0 |  | 367.3035
| 4 | 1 | 750 | 925 | 100 | 7.9939 | 14.7887 | 0 | -11.4104 | -74.8627 | 303.2523 | -5.9363 | -118.5311 | 0 |  | -95.6929
| 5 | 3 | 500 | 350 | 100 | 166.3117 | 102.5589 | 0 | 0 | 0 | -5.9363 | 17.1746 | 0 | -2.5321 |  | 8.8135
| 6 | 2 | 500 | 671 | 100 | 150.5943 | 139.2997 | 0 | 0 | 0 | -118.5311 | 0 | 208.5112 | -5.7003 |  | 182.1688
| 7 | 1 | 500 | 400 | 100 | 24.9024 | 46.0694 | 0 | 0 | 0 | 0 | -2.5321 | -5.7003 | 11.5559 |  | 1.3268
| 8 | 1 | 500 | 650 | 100 | 40.4663 | 74.8627
| 9 | 1 | 750 | 1000 | 120 | 6.1678 | 11.4104 | Inverted Matrix
| 10 | 6 | 1000 | 1000 | 120 | 41.808 | 12.8908 | 0.01284 | 0.0084667 | 0.0014589 | 0.0008861 | 0.00035504 | 0.00051276 | 0.00033073 | ΔQ1 | -1.1068
| 11 | 6 | 1000 | 925 | 120 | 38.6724 | 11.924 | 0.0084667 | 0.01525 | 0.0010557 | 0.0010893 | 0.00043647 | 0.00063037 | 0.00040659 | ΔQ2 | 1.5277
| 12 | 6 | 1000 | 800 | 120 | 33.4464 | 10.3126 | 0.0014589 | 0.0010557 | 0.0028028 | 0.00095519 | 0.00038272 | 0.00055274 | 0.00035652 | ΔQ3 | 0.87608
| 13 | 1 | 750 | 763 | 120 | 4.706 | 8.7062 | 0.0008861 | 0.0010893 | 0.00095519 | 0.0046664 | 0.0018697 | 0.0027003 | 0.0017417 | ΔQ4 | 0.41659
| 14 | 4 | 1000 | 650 | 120 | 12.8352 | 5.9363 | 0.00035504 | 0.00043647 | 0.00038272 | 0.0018697 | 0.060946 | 0.0014475 | 0.014069 | ΔQ5 | 0.78179
| 15 | 0.5 | 750 | 400 | 120 | 0.68436 | 2.5321 | 0.00051276 | 0.00063037 | 0.00055274 | 0.0027003 | 0.0014475 | 0.0064263 | 0.0034871 | ΔQ6 | 1.1336
| 16 | 0.5 | 750 | 125 | 120 | 0.21386 | 0.79129 | 0.00033073 | 0.00040659 | 0.00035652 | 0.0017417 | 0.014069 | 0.0034871 | 0.091339 | ΔQ7 | 0.8453
| 17 | 0.5 | 750 | 400 | 120 | 0.68436 | 2.5321
| 18 | 0.5 | 500 | 125 | 120 | 1.5406 | 5.7003
| 19 | 1 | 500 | 800 | 120 | 35.5455 | 65.7593
| 20 | 2 | 500 | 125 | 120 | 20.0221 | 18.5205
| 21 | 2 | 500 | 800 | 120 | 128.1418 | 118.5311
| 22 | 1 | 500 | 1000 | 120 | 44.4319 | 82.1991
Iteration
2 | Pipe | Flow | Diameter | Length | C | Head Loss
|  | m3/s | mm | m |  | HL, m | nHL/Q | Coefficient Matrix | [7 empty] | F
| 1 | -0.10677 | 1000 | 1000 | 100 | -0.033947 | 0.58819 | 86.1581 | -41.488 | -16.2205 | 0 | 0 | 0 | 0 |  | -52.6303
| 2 | 3.3655 | 750 | 925 | 100 | 75.4746 | 41.488 | -41.488 | 67.7522 | 0 | -1.7631 | 0 | 0 | 0 |  | 40.8067
| 3 | 1.0171 | 750 | 1000 | 100 | 8.9181 | 16.2205 | -16.2205 | 0 | 289.0847 | -103.2376 | 0 | 0 | 0 |  | 67.6382
| 4 | 2.1068 | 750 | 925 | 100 | 31.7285 | 27.8615 | 0 | -1.7631 | -103.2376 | 254.6578 | -5.4723 | -81.2736 | 0 |  | -7.0369
| 5 | 2.1239 | 500 | 350 | 100 | 87.7915 | 76.4693 | 0 | 0 | 0 | -5.4723 | 22.5005 | 0 | -2.803 |  | -2.095
| 6 | 1.1239 | 500 | 671 | 100 | 51.8513 | 85.349 | 0 | 0 | 0 | -81.2736 | 0 | 110.6446 | -8.3938 |  | 56.1896
| 7 | 0.12392 | 500 | 400 | 100 | 0.52302 | 7.8085 | 0 | 0 | 0 | 0 | -2.803 | -8.3938 | 14.8807 |  | 1.0432
| 8 | 1.4595 | 500 | 650 | 100 | 81.4458 | 103.2376
| 9 | -0.11114 | 750 | 1000 | 120 | -0.10592 | 1.7631 | Inverted Matrix
| 10 | 4.4723 | 1000 | 1000 | 120 | 24.2749 | 10.0415 | 0.016797 | 0.010305 | 0.0012113 | 0.00075279 | 0.0002293 | 0.0005811 | 0.00037098 | ΔQ1 | -0.35431
| 11 | 7.5277 | 1000 | 925 | 120 | 58.8368 | 14.4596 | 0.010305 | 0.021086 | 0.00080376 | 0.00063156 | 0.00019237 | 0.00048752 | 0.00031123 | ΔQ2 | 0.39534
| 12 | 6.4166 | 1000 | 800 | 120 | 37.8688 | 10.9182 | 0.0012113 | 0.00080376 | 0.0043783 | 0.0023832 | 0.00072594 | 0.0018397 | 0.0011745 | ΔQ3 | 0.35149
| 13 | 1.7818 | 750 | 763 | 120 | 13.7006 | 14.2251 | 0.00075279 | 0.00063156 | 0.0023832 | 0.0065552 | 0.0019967 | 0.0050602 | 0.0032304 | ΔQ4 | 0.38474
| 14 | 3.6348 | 1000 | 650 | 120 | 10.7518 | 5.4723 | 0.0002293 | 0.00019237 | 0.00072594 | 0.0019967 | 0.046169 | 0.0022215 | 0.0099497 | ΔQ5 | 0.069312
| 15 | 0.56351 | 750 | 400 | 120 | 0.8538 | 2.803 | 0.0005811 | 0.00048752 | 0.0018397 | 0.0050602 | 0.0022215 | 0.013358 | 0.0079535 | ΔQ6 | 0.83237
| 16 | 1.3453 | 750 | 125 | 120 | 1.3346 | 1.8353 | 0.00037098 | 0.00031123 | 0.0011745 | 0.0032304 | 0.0099497 | 0.0079535 | 0.073562 | ΔQ7 | 0.55268
| 17 | -0.3453 | 750 | 400 | 120 | -0.34503 | 1.8486
| 18 | 0.78829 | 500 | 125 | 120 | 3.5766 | 8.3938
| 19 | -0.13359 | 500 | 800 | 120 | -0.85796 | 11.8813
| 20 | 0.86641 | 500 | 125 | 120 | 4.2598 | 9.0958
| 21 | 1.283 | 500 | 800 | 120 | 56.3644 | 81.2736
| 22 | 0.58341 | 500 | 1000 | 120 | 16.3963 | 51.993
Iteration
3 | Pipe | Flow | Diameter | Length | C | Head Loss
|  | m3/s | mm | m |  | HL, m | nHL/Q | Coefficient Matrix | [7 empty] | F
| 1 | -0.46108 | 1000 | 1000 | 100 | -0.50834 | 2.0396 | 73.2553 | -33.4889 | -5.9298 | 0 | 0 | 0 | 0 |  | -5.5418
| 2 | 2.6158 | 750 | 925 | 100 | 47.3523 | 33.4889 | -33.4889 | 59.7784 | 0 | -1.9051 | 0 | 0 | 0 |  | 3.0012
| 3 | 0.31134 | 750 | 1000 | 100 | 0.99794 | 5.9298 | -5.9298 | 0 | 247.877 | -101.2351 | 0 | 0 | 0 |  | 10.0693
| 4 | 2.4611 | 750 | 925 | 100 | 42.3001 | 31.7971 | 0 | -1.9051 | -101.2351 | 197.7317 | -5.8734 | -56.4353 | 0 |  | 0.20613
| 5 | 1.7724 | 500 | 350 | 100 | 62.8202 | 65.5697 | 0 | 0 | 0 | -5.8734 | 25.313 | 0 | -4.7454 |  | 0.52375
| 6 | 0.77242 | 500 | 671 | 100 | 25.9082 | 62.0515 | 0 | 0 | 0 | -56.4353 | 0 | 131.7336 | -10.8657 |  | -14.1186
| 7 | -0.22758 | 500 | 400 | 100 | -1.6104 | 13.0909 | 0 | 0 | 0 | 0 | -4.7454 | -10.8657 | 22.2353 |  | -0.95725
| 8 | 1.4262 | 500 | 650 | 100 | 78.0467 | 101.2351
| 9 | -0.12174 | 750 | 1000 | 120 | -0.12537 | 1.9051 | Inverted Matrix
| 10 | 4.0769 | 1000 | 1000 | 120 | 20.4548 | 9.2818 | 0.01843 | 0.010341 | 0.00064422 | 0.00049785 | 0.00014179 | 0.00022484 | 0.00014013 | ΔQ1 | -0.067747
| 11 | 7.9231 | 1000 | 925 | 120 | 64.6805 | 15.1026 | 0.010341 | 0.022538 | 0.00046223 | 0.00052606 | 0.00014982 | 0.00023758 | 0.00014807 | ΔQ2 | 0.011681
| 12 | 6.8013 | 1000 | 800 | 120 | 42.1762 | 11.4722 | 0.00064422 | 0.00046223 | 0.0053481 | 0.0031793 | 0.00090547 | 0.0014358 | 0.00089489 | ΔQ3 | 0.03167
| 13 | 1.8511 | 750 | 763 | 120 | 14.7029 | 14.6941 | 0.00049785 | 0.00052606 | 0.0031793 | 0.0077555 | 0.0022088 | 0.0035025 | 0.002183 | ΔQ4 | -0.017952
| 14 | 3.9502 | 1000 | 650 | 120 | 12.5413 | 5.8734 | 0.00014179 | 0.00014982 | 0.00090547 | 0.0022088 | 0.041853 | 0.0017537 | 0.0097891 | ΔQ5 | -0.0029727
| 15 | 1.0469 | 750 | 400 | 120 | 2.6853 | 4.7454 | 0.00022484 | 0.00023758 | 0.0014358 | 0.0035025 | 0.0017537 | 0.0095056 | 0.0050193 | ΔQ6 | -0.12344
| 16 | 1.898 | 750 | 125 | 120 | 2.5228 | 2.459 | 0.00014013 | 0.00014807 | 0.00089489 | 0.002183 | 0.0097891 | 0.0050193 | 0.049515 | ΔQ7 | -0.10401
| 17 | -0.89798 | 750 | 400 | 120 | -2.0218 | 4.1652
| 18 | 1.068 | 500 | 125 | 120 | 6.2726 | 10.8657
| 19 | -0.96596 | 500 | 800 | 120 | -33.3398 | 63.8519
| 20 | 0.034035 | 500 | 125 | 120 | 0.010683 | 0.58066
| 21 | 0.83536 | 500 | 800 | 120 | 25.4832 | 56.4353
| 22 | 0.19867 | 500 | 1000 | 120 | 2.2349 | 20.8105
Iteration
4 | Pipe | Flow | Diameter | Length | C | Head Loss
|  | m3/s | mm | m |  | HL, m | nHL/Q | Coefficient Matrix | [7 empty] | F
| 1 | -0.52883 | 1000 | 1000 | 100 | -0.65509 | 2.2917 | 71.7298 | -32.6225 | -4.276 | 0 | 0 | 0 | 0 |  | -0.082061
| 2 | 2.5364 | 750 | 925 | 100 | 44.7267 | 32.6225 | -32.6225 | 59.296 | 0 | -2.2927 | 0 | 0 | 0 |  | 0.028626
| 3 | 0.21192 | 750 | 1000 | 100 | 0.48984 | 4.276 | -4.276 | 0 | 247.576 | -104.2212 | 0 | 0 | 0 |  | 0.033009
| 4 | 2.5288 | 750 | 925 | 100 | 44.4794 | 32.5395 | 0 | -2.2927 | -104.2212 | 208.6516 | -5.8545 | -62.4384 | 0 |  | -0.22375
| 5 | 1.7408 | 500 | 350 | 100 | 60.7594 | 64.5725 | 0 | 0 | 0 | -5.8545 | 24.8817 | 0 | -4.3532 |  | 0.019876
| 6 | 0.74076 | 500 | 671 | 100 | 23.9773 | 59.8823 | 0 | 0 | 0 | -62.4384 | 0 | 132.1169 | -10.6974 |  | -0.015607
| 7 | -0.25924 | 500 | 400 | 100 | -2.0493 | 14.624 | 0 | 0 | 0 | 0 | -4.3532 | -10.6974 | 21.146 |  | -0.045555
| 8 | 1.4759 | 500 | 650 | 100 | 83.1442 | 104.2212
| 9 | -0.15137 | 750 | 1000 | 120 | -0.18759 | 2.2927 | Inverted Matrix
| 10 | 4.0653 | 1000 | 1000 | 120 | 20.3465 | 9.2592 | 0.018644 | 0.010274 | 0.00050416 | 0.00043269 | 0.00012539 | 0.0002154 | 0.00013478 | ΔQ1 | -0.001323
| 11 | 7.9347 | 1000 | 925 | 120 | 64.8571 | 15.1215 | 0.010274 | 0.022537 | 0.00040122 | 0.00053156 | 0.00015404 | 0.00026462 | 0.00016558 | ΔQ2 | -0.00031222
| 12 | 6.7834 | 1000 | 800 | 120 | 41.9705 | 11.4464 | 0.00050416 | 0.00040122 | 0.0053962 | 0.003203 | 0.00092821 | 0.0015945 | 0.00099773 | ΔQ3 | -0.00062032
| 13 | 1.8481 | 750 | 763 | 120 | 14.6592 | 14.674 | 0.00043269 | 0.00053156 | 0.003203 | 0.007591 | 0.0021998 | 0.003779 | 0.0023646 | ΔQ4 | -0.001736
| 14 | 3.9352 | 1000 | 650 | 120 | 12.4535 | 5.8545 | 0.00012539 | 0.00015404 | 0.00092821 | 0.0021998 | 0.042396 | 0.0018209 | 0.0096489 | ΔQ5 | -9.2771e-05
| 15 | 0.94584 | 750 | 400 | 120 | 2.2256 | 4.3532 | 0.0002154 | 0.00026462 | 0.0015945 | 0.003779 | 0.0018209 | 0.0097862 | 0.0053255 | ΔQ6 | -0.0011621
| 16 | 1.794 | 750 | 125 | 120 | 2.273 | 2.344 | 0.00013478 | 0.00016558 | 0.00099773 | 0.0023646 | 0.0096489 | 0.0053255 | 0.051971 | ΔQ7 | -0.0027613
| 17 | -0.79397 | 750 | 400 | 120 | -1.61 | 3.7514
| 18 | 1.0485 | 500 | 125 | 120 | 6.0631 | 10.6974
| 19 | -0.84252 | 500 | 800 | 120 | -25.8886 | 56.846
| 20 | 0.15748 | 500 | 125 | 120 | 0.18175 | 2.1351
| 21 | 0.94086 | 500 | 800 | 120 | 31.7543 | 62.4384
| 22 | 0.21662 | 500 | 1000 | 120 | 2.6227 | 22.3984
Iteration
5 | Pipe | Flow | Diameter | Length | C | Head Loss
|  | m3/s | mm | m |  | HL, m | nHL/Q | Coefficient Matrix | [7 empty] | F
| 1 | -0.53015 | 1000 | 1000 | 100 | -0.65812 | 2.2966 | 71.726 | -32.6115 | -4.264 | 0 | 0 | 0 | 0 |  | 2.9753e-06
| 2 | 2.5354 | 750 | 925 | 100 | 44.6938 | 32.6115 | -32.6115 | 59.3033 | 0 | -2.311 | 0 | 0 | 0 |  | -7.4423e-06
| 3 | 0.21122 | 750 | 1000 | 100 | 0.48684 | 4.264 | -4.264 | 0 | 247.6633 | -104.2882 | 0 | 0 | 0 |  | -2.3061e-05
| 4 | 2.5302 | 750 | 925 | 100 | 44.5225 | 32.554 | 0 | -2.311 | -104.2882 | 208.8524 | -5.8524 | -62.406 | 0 |  | 0.00016962
| 5 | 1.7414 | 500 | 350 | 100 | 60.7994 | 64.592 | 0 | 0 | 0 | -5.8524 | 24.8686 | 0 | -4.3427 |  | 1.561e-05
| 6 | 0.74138 | 500 | 671 | 100 | 24.0145 | 59.9249 | 0 | 0 | 0 | -62.406 | 0 | 132.0451 | -10.7112 |  | -3.2752e-05
| 7 | -0.25862 | 500 | 400 | 100 | -2.0402 | 14.5942 | 0 | 0 | 0 | 0 | -4.3427 | -10.7112 | 21.1352 |  | -2.2392e-05
| 8 | 1.477 | 500 | 650 | 100 | 83.2606 | 104.2882
| 9 | -0.1528 | 750 | 1000 | 120 | -0.19087 | 2.311 | Inverted Matrix
| 10 | 4.0656 | 1000 | 1000 | 120 | 20.3494 | 9.2598 | 0.01864 | 0.010267 | 0.00050315 | 0.00043275 | 0.00012541 | 0.00021547 | 0.00013497 | ΔQ1 | 3.2728e-08
| 11 | 7.9344 | 1000 | 925 | 120 | 64.8523 | 15.121 | 0.010267 | 0.022529 | 0.00040138 | 0.00053341 | 0.00015458 | 0.00026559 | 0.00016636 | ΔQ2 | -6.591e-08
| 12 | 6.7816 | 1000 | 800 | 120 | 41.9506 | 11.4439 | 0.00050315 | 0.00040138 | 0.0053938 | 0.0031998 | 0.0009273 | 0.0015932 | 0.00099798 | ΔQ3 | 3.5683e-07
| 13 | 1.848 | 750 | 763 | 120 | 14.6579 | 14.6734 | 0.00043275 | 0.00053341 | 0.0031998 | 0.0075813 | 0.002197 | 0.0037748 | 0.0023645 | ΔQ4 | 1.0672e-06
| 14 | 3.9336 | 1000 | 650 | 120 | 12.4438 | 5.8524 | 0.00012541 | 0.00015458 | 0.0009273 | 0.002197 | 0.042411 | 0.0018201 | 0.0096368 | ΔQ5 | 7.3713e-07
| 15 | 0.94317 | 750 | 400 | 120 | 2.214 | 4.3427 | 0.00021547 | 0.00026559 | 0.0015932 | 0.0037748 | 0.0018201 | 0.00979 | 0.0053355 | ΔQ6 | 1.9051e-07
| 16 | 1.7912 | 750 | 125 | 120 | 2.2665 | 2.3409 | 0.00013497 | 0.00016636 | 0.00099798 | 0.0023645 | 0.0096368 | 0.0053355 | 0.051998 | ΔQ7 | -8.1147e-07
| 17 | -0.79121 | 750 | 400 | 120 | -1.5997 | 3.7403
| 18 | 1.0501 | 500 | 125 | 120 | 6.0802 | 10.7112
| 19 | -0.84136 | 500 | 800 | 120 | -25.8226 | 56.7794
| 20 | 0.15864 | 500 | 125 | 120 | 0.18424 | 2.1485
| 21 | 0.94028 | 500 | 800 | 120 | 31.7185 | 62.406
| 22 | 0.21836 | 500 | 1000 | 120 | 2.6617 | 22.5509
12 m3/s
1
3
6
2
5
9
4
7
8
10
1
2
3
4
5
6
7
11
12
13
14
15
16
17
18
19
20
21
22
2 m3/s
1 m3/s
1 m3/s
1 m3/s
1 m3/s
1 m3/s
1 m3/s
1 m3/s
1 m3/s
1 m3/s
1 m3/s
1 m3/s
1 m3/s
1 m3/s
1 m3/s